- GENERAL:-

| LOCATION- SUBSTATION: 15 |  | CUBICAL NO. : 12 | LCP NO.: 5207 |
| --- | --- | --- | --- |
| CB NO: 12 | FEEDER: CEFS MOTOR NO. 01 |  |  |

CIRCUIT BREAKER

2.1 NAME PLATE DETAILS :-

| Make | SCHNEIDER ELECTRIC |
| --- | --- |
| Type | SE-ECOFIT-NGEF-7512-1 |
| Sl. No. | 22223921460/04 |
| Rated Voltage | 11 KV |
| Rated Current | 1250 A |
| Control Voltage | 110 VDC |

2.2INSULATION RESISTANCE TEST: (MEASURED VALUES IN GΩ)

| Reference | Breaker Condition | Applied Voltage (V) | R phase | Y phase | B phase |
| --- | --- | --- | --- | --- | --- |
| Pole – Pole’ | Open | 5000 | >500 | >500 | >500 |
| Phase – Phase | Close | 5000 | >500 | >500 | >500 |
| Pole – Earth | Close | 5000 | >500 | >500 | >500 |

2.3 COIL RESISTANCE TEST:

| Terminal Reference | Measured Resistance in Ω |
| --- | --- |
| Closing coil | 63.9 |
| Tripping Coil | 110.3 |
| Spring charge motor | 1.432 KΩ |

2.4 CONTACT RESISTANCE TEST: 			            Applied Current (100A)

| Phase Ref. | Measured Resistance in Micro ohms |
| --- | --- |
| R | 22.0 |
| Y | 29.0 |
| B | 23.0 |

2.5 TIME INTERVAL TEST:

| Operation Ref. | Measured Time in milli Seconds |  |  |
| --- | --- | --- | --- |
|  | R | Y | B |
| Close | 32 | 32 | 32 |
| Open | 36 | 36 | 36 |
| Close – Open | 40 | 40 | 40 |

CURRENT TRANSFORMER

3. RATIO TEST: (BY PRIMARY INJECTION)

3.1 CT (CTR:    150 / 5    A)

| Phase Ref. | Injected current in Primary (A) | Measured current in Secondary ( A ) |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | RELAY | ENERGY METER | ICT | AMMETER |
| R | 150 | 150 | 150 | - | - |
| Y | 150 | 150 | - | - | 150 |
| B | 150 | 150 | 150 | - | - |

3.2 CBCT (RATIO:     100    /   1  A)

| Injected current in Primary (A) | Measured current in Secondary (mA) |
| --- | --- |
| 10 | 103.5 |

RELAY

| MAKE | MICOM |
| --- | --- |
| MODEL | P24291TA6S0700K |
| SL. NO. | 35588640/02/22 |

4.0 PROTECTION TESTING ( BY SECONDARY INJECTION)

4.1  MEASUREMENTS:-

| REF | INJECTED (A) | MEASURED(A) IN RELAY |
| --- | --- | --- |
| R | 5 | 150.0 |
| Y | 5 | 149.8 |
| B | 5 | 150.1 |

4.2 SHORT CIRCUIT: I>1

`			 	Set Current =  825.00 A       CURVE:    DT,	Delay =  40 mSec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| RYB | 27.5 | 0.126 |

4.3 THERMAL O/L: Ith

Set Current =        90  A		Time const.= 45 min

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| RYB | 18 | 75.65 |

4.4 NEGATIVE SEQUENCE: I2>1

STAGE 1:	Set Current =     26.25  A	CURVE: DT ,   Delay =       4 Sec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| RYB | 1 | 4.013 |

I2>2       STAGE 2: 	Set Current =      45  A		      	TMS =   2.00

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| RYB | 10 | 1.212 |

4.5 PROLONGED START/ STARTUP CRITERIA: NOT DONE.

Mode=	I²T	,    Motor St. Criteria Current=  225.0 A     	Time =  110.0 Sec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| RYB | - | - |

4.6 JAMMING PROTECTION:

Set Current =   225 A			Time =    4 Sec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| RYB | 8 | 4.033 |

4.7 EARTH FAULT PROTECTION (E/F): OPERATED THROUGH CBCT

Set Current =  2.52 A		Time =     500  mSec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| Io | 2.52 | OPERATED |

POTENTIAL TRANSFORMER

5.0 VOLTAGE RATIO:

| REFERENCE | APPLIED VOLTAGE(V) | MEASURED VOLTAGE (V) |  |
| --- | --- | --- | --- |
|  |  | a1-a2 | - |
| R | 240.1 | 2.495 | - |
| G | 240.2 | 2.494 | - |
| Y | 240.5 | 2.496 | - |

5.1 WINDING RESISTANCE :

| REFERENCE | MEASURED RESISTANCE Ω |  |
| --- | --- | --- |
|  | a1-a2 |  |
| R | 0.3 |  |
| G | 0.3 |  |
| Y | 0.3 |  |

6.0 FINAL CHECKS

| S N | OBSERVATION | STATUS | RESULT |
| --- | --- | --- | --- |
| 1 | Complete Tightness Of Relay Panel | DONE | OK |
| 2 | Relay Measurement Testing | DONE | OK |
| 3 | Relay Protection Testing | DONE | OK |
| 4 | Relay Indications (ON/OFF/Trip) | DONE | OK |
| 5 | Relay Communication (RXD & TXD) | - | - |
| 6 | Binary Input & Binary Output Checking | - | - |
| 7 | Cleaning of Auxiliary Relay | DONE | OK |
| 8 | Cleaning of PCB cards of Numerical Relay (if required) | - | - |
| 9 | Consolidate data & Control Scheme Checked | DONE | OK |
| 10 | Trip of CB through Master Checked | DONE | OK |
| 11 | Field Simulation of OTI/WTI/BUCH Fault Checked./ Motor Checked | - | - |
| 12 | All CT Links Closed & Tightness Check after Testing | DONE | OK |
| 13 | All Protection Settings Normalized after Testing | DONE | OK |
| 14 | Testing DR Downloaded from the RELAY | - | - |
| 15 | Auxiliary Relay (HR & SR) operation check. | - | - |

7.0 REMARKS:   1) All test results are found satisfactory.