- GENERAL

| LOCATION- SUBSTATION: 15 |  | CUBICAL NO. : 632 | LCP NO.: 13266 |
| --- | --- | --- | --- |
| CB NO: 632 | FEEDER: SWP – 7D |  |  |

CIRCUIT BREAKER

2.1 NAME PLATE DETAILS :-

| Make | SIEMENS |
| --- | --- |
| Type | 3AH 3116-2 |
| Sl. No. | N8 29935 |
| Rated Voltage | 12 KV |
| Rated Current | 1250 A |
| Control Voltage | 110V DC |

2.2INSULATION RESISTANCE TEST: (MEASURED VALUES IN GΩ)

| Reference | Breaker Condition | Applied Voltage (V) | R phase | Y phase | B phase |
| --- | --- | --- | --- | --- | --- |
| Pole – Pole’ | Open | 5000 | >500 | >500 | >500 |
| Phase – Phase | Close | 5000 | >500 | >500 | >500 |
| Pole – Earth | Close | 5000 | >500 | >500 | >500 |

2.3 COIL RESISTANCE TEST:

| Terminal Reference | Measured Resistance in Ω |
| --- | --- |
| Closing coil | 93.0 |
| Tripping Coil | 63.0 |
| Spring charge motor | 0.833 MΩ |

2.4 CONTACT RESISTANCE TEST: 			            Applied Current (100A)

| Phase Ref. | Measured Resistance in Micro ohms |
| --- | --- |
| R | 32.3 |
| Y | 30.3 |
| B | 31.6 |

2.5 TIME INTERVAL TEST:

| Operation Ref. | Measured Time in milli Seconds |  |  |
| --- | --- | --- | --- |
|  | R | Y | B |
| Close | 61 | 61 | 61 |
| Open | 53 | 53 | 53 |
| Close – Open | 56 | 56 | 56 |

CURRENT TRANSFORMER

3. RATIO TEST: (BY PRIMARY INJECTION)

3.1 CT (CTR:    50 / 5    A)

| Phase Ref. | Injected current in Primary (A) | Measured current in Secondary ( A ) |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | RELAY | ENERGY METER | ICT | AMMETER |
| R | 50 | 100 % | 50 | - | 50 |
| Y | 50 | 100 % | - | - | 50 |
| B | 50 | 100 % | 50 | - | 50 |

3.2 CBCT (RATIO:     200    /   1  A)

| Injected current in Primary (A) | Measured current in Secondary (mA) |
| --- | --- |
| 10 | 58.0 |

RELAY

| MAKE | SIEMENS |
| --- | --- |
| MODEL | 7SJ6025-5EB20-1HAO/CC |
| SL. NO. | BF0711059557 |

4.0 PROTECTION TESTING ( BY SECONDARY INJECTION)

4.1  MEASUREMENTS:-

| REF | INJECTED (A) | MEASURED(A) IN RELAY |
| --- | --- | --- |
| R | 5 | 100 % |
| Y | 5 | 100 % |
| B | 5 | 100 % |

4.2 SHORT CIRCUIT: 50/51 OC	 I>>>

`			 	Set Current =       9.60    x In	   CURVE:    DT,	Delay = 0 mSec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| RYB | 48 | OPERATED |

I>>	Set Current =       7.0    x In	   CURVE:    DT,	Delay =  80 mSec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| RYB | 35 | 0.126 |

4.3 THERMAL O/L: 49

Set Current =        0.70   x In		Time const.=      10 min

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| RYB | 21 | 17.015 |

4.4 NEGATIVE SEQUENCE: I2>

STAGE 1:	Set Current =     14%  x In      CURVE: DT ,   Delay =       10 Sec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| RYB | 1.0 | 10.060 |

I2>>       STAGE 2: 	Set Current =      56%    x In       CURVE:    DT           Time = 1 sec

| Phase | Injected Current (A) X6 | Operated Time (Sec) |
| --- | --- | --- |
| RYB | 16.8 | 1.057 |

4.5 PROLONGED START/ STARTUP SUPERVISION:	  48

Mode=	I²T	,    Motor St. Criteria Current=  1.2   x In A      Time =       30 Sec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| RYB | 6.5 | 30.095 |

4.6 EARTH FAULT PROTECTION (E/F): OPERATED THROUGH CBCT

Set Current =     1 %		Time =     1    Sec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| Io | 2.4 | OPERATED |

VACUUM   CONTACTOR (NA)

5.0 NAME PLATE DETAILS :-

| Make | - |
| --- | --- |
| Type | - |
| Sl. No. | - |
| Rated Voltage | - |
| Rated Current | - |
| Control Voltage | - |

5.1 CONTACT RESISTANCE TEST: 			            Applied Current (100A)

| Phase Ref. | Measured Resistance in Micro ohms |
| --- | --- |
| R |  |
| Y |  |
| B |  |

6.0 FINAL CHECKS

| S N | OBSERVATION | STATUS | RESULT |
| --- | --- | --- | --- |
| 1 | Complete Tightness Of Relay Panel | DONE | OK |
| 2 | Relay Measurement Testing | DONE | OK |
| 3 | Relay Protection Testing | DONE | OK |
| 4 | Relay Indications (ON/OFF/Trip) | DONE | OK |
| 5 | Relay Communication (RXD & TXD) | - | - |
| 6 | Binary Input & Binary Output Checking | - | - |
| 7 | Cleaning of Auxiliary Relay | DONE | OK |
| 8 | Cleaning of PCB cards of Numerical Relay (if required) | - | - |
| 9 | Consolidate data & Control Scheme Checked | DONE | OK |
| 10 | Trip of CB through Master Checked | DONE | OK |
| 11 | Field Simulation of OTI/WTI/BUCH Fault Checked./ Motor Checked | - | - |
| 12 | All CT Links Closed & Tightness Check after Testing | DONE | OK |
| 13 | All Protection Settings Normalized after Testing | DONE | OK |
| 14 | Testing DR Downloaded from the RELAY | - | - |
| 15 | Auxiliary Relay (HR & SR) operation check. | DONE | OK |

7.0 REMARKS:  1) All test results are found satisfactory.

2) TECH Trip relay healthiness checked found ok.