- GENERAL

| LOCATION- SUBSTATION:21 |  | CUBICAL NO. : 59B | LCP NO. :10141 |
| --- | --- | --- | --- |
| CB NO: -39 | FEEDER: MOT SHUNT EXT.3 SHUNT (2000KW) |  |  |

CIRCUIT BREAKER

2.1 NAME PLATE DETAILS: -

| Make | SIEMENS |
| --- | --- |
| Type | 3AH3116-3 |
| Sl. No. | N8 23734 |
| Rated Voltage | 7.5 kV |
| Rated Current | 1250 A |
| Control Voltage | 220 VDC |

2.2INSULATION RESISTANCE TEST: (MEASURED VALUES IN GΩ)

| Reference | Breaker Condition | Applied Voltage (V) | R phase | Y phase | B phase |
| --- | --- | --- | --- | --- | --- |
| Pole – Pole’ | Open | 5000 | >500 | >500 | >500 |
| Phase – Phase | Close | 5000 | >500 | >500 | >500 |
| Pole – Earth | Close | 5000 | >500 | >500 | >500 |

2.3 COIL RESISTANCE TEST:

| Terminal Reference | Measured Resistance in Ω |
| --- | --- |
| Closing coil | 35 Ω |
| Tripping Coil | 43 Ω |
| Spring charge motor | 25 Ω |

2.4 CONTACT RESISTANCE TEST: 			            Applied Current (100A)

| Phase Ref. | Measured Resistance in Micro ohms |
| --- | --- |
| R | 59.3 |
| Y | 59.4 |
| B | 57.4 |

2.5 TIME INTERVAL TEST:

| Operation Ref. | Measured Time in milli Seconds |  |  |
| --- | --- | --- | --- |
|  | R | Y | B |
| Close | 53 | 53 | 53 |
| Open | 46 | 46 | 46 |
| Close – Open | 49 | 49 | 49 |

CURRENT TRANSFORMER

3. RATIO TEST: (BY PRIMARY INJECTION)

3.1 CT (CTR:  300/1A)

| Phase Ref. | Injected current in Primary (A) | Measured current in Secondary ( A ) |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | RELAY | ENERGY METER | ICT | AMMETER |
| R | 300.1 | 300.1 | - | 1.0 | - |
| Y | 300.0 | 300.0 | - | 1.0 | 300 |
| B | 300.3 | 300.0 | - | 1.0 | - |

3.2 CBCT (RATIO: 50/1 A)

| Injected current in Primary (A) | Status |
| --- | --- |
| 4.0 | Operated |

RELAY

| MAKE | SIEMENS |
| --- | --- |
| MODEL | 7SK8042-5EB90 |
| SL. NO. | BE1006091363 |

4.0 PROTECTION TESTING ( BY SECONDARY INJECTION)

4.1 MEASUREMENTS: -

| REF | INJECTED (A) | MEASURED(A) IN RELAY |
| --- | --- | --- |
| R | 1.0 | 301 |
| Y | 1.0 | 300 |
| B | 1.0 | 300 |

4.2 OVER CURRENT (50-2):

Set Current = 6.70x In                          	Delay = 0.050   Sec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| RYB | 6.70 | 0.091 |

4.3 THERMAL O/L (49):

Set Current = 0.68 x In		Time const.= 3.8 Sec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| RYB | 4.08 | 6.521 |

4.4 NEGATIVE SEQUENCE (46-1):

Set Current = 1.34 x In	              	Delay = 1.0 Sec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| RYB | 1.34 | 1.07 |

Set Current =0.20xIn		    		TMS =   0.45 Sec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| RYB | 1.6 | 1.67 |

4.5 Staling During Start/ During Run:

Set Current = 2.80 x In	   Lock Rotor Time=5. 0Sec	St.upTime  = 55.0 Sec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| RYB | 2.80 | 53.21 |

4.6 Stalling During Run/Lock Jam:

Set Current = 1.34x In		Time = 4.0 Sec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| RYB | 1.34 | 4.01 |

6.0 FINAL CHECKS

| S N | OBSERVATION | STATUS | RESULT |
| --- | --- | --- | --- |
| 1 | Complete Tightness Of Relay Panel | DONE | OK |
| 2 | Relay Measurement Testing | DONE | OK |
| 3 | Relay Protection Testing | DONE | OK |
| 4 | Relay Indications (ON/OFF/Trip) | DONE | OK |
| 5 | Relay Communication (RXD & TXD) | - | - |
| 6 | Binary Input & Binary Output Checking | DONE | OK |
| 7 | Cleaning of Auxiliary Relay | DONE | OK |
| 8 | Cleaning of PCB cards of Numerical Relay (if required) | - | - |
| 9 | Consolidate data & Control Scheme Checked | DONE | OK |
| 10 | Trip of CB through Master Checked | DONE | OK |
| 11 | Field Simulation of OTI/WTI/BUCH Fault Checked./ Motor Checked | - | - |
| 12 | All CT Links Closed & Tightness Check after Testing | DONE | OK |
| 13 | All Protection Settings Normalized after Testing | DONE | OK |
| 14 | Testing DR Downloaded from the RELAY | - | - |
| 15 | Auxiliary Relay (HR & SR) operation check. | DONE | OK |

6.0 REMARKS:   1) All test results are found satisfactory.