CUBICLE FEEDER

- GENERAL

| LOCATION- SUBSTATION: 26 |  | CUBICAL NO.: 604 | LCP NO.: 19988 |
| --- | --- | --- | --- |
| CB NO: NA | FEEDER :- BOOSTER FAN – 1D |  |  |

CIRCUIT BREAKER

2.1 Name Plate Details :-

| Make | ABB |
| --- | --- |
| Type | HCA 12/1240 |
| Sl. No. | V3541 |
| Rated Voltage | 12 KV |
| Rated Current | 1250 A |
| Control Voltage | 110 VDC |

2.2 NSULATION RESISTANCE TEST:- (MEASURED VALUES IN GΩ)

| Reference | Breaker Condition | Applied Voltage (V) | R phase | Y phase | B phase |
| --- | --- | --- | --- | --- | --- |
| Pole – Pole’ | Open | 5000 | >500 | >500 | >500 |
| Phase – Phase | Close | 5000 | >500 | >500 | >500 |
| Pole – Earth | Close | 5000 | >500 | >500 | >500 |

2.3 COIL RESISTANCE TEST:-

| Terminal Reference | Measured Resistance in Ω |
| --- | --- |
| Closing coil | 73.6 |
| Tripping Coil | 70.6 |
| Spring charge motor | Faulty |

2.4 CONTACT RESISTANCE TEST:- 			            Applied Current (100A)

| Phase Ref. | Measured Resistance in Micro ohms |
| --- | --- |
| R | 42.54 |
| Y | 34.3 |
| B | 46.5 |

2.5 TIME INTERVAL TEST:-

| Operation Ref. | Measured Time in milli Seconds |  |  |
| --- | --- | --- | --- |
|  | R | Y | B |
| Close | 41 | 41 | 41 |
| Open | 36 | 36 | 36 |
| Close – Open | 45 | 45 | 45 |

CURRENT TRANSFORMER

3. RATIO TEST:- (BY PRIMARY INJECTION)

3.1 CT (CTR:-   100  / 5  A )

| Phase Ref. | Injected current in Primary (A) | Measured current in Secondary Side ( A ) |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | RELAY | ENERGY METER | TRANSDUCER (P) | AMMETER |
| R | 100 | 5 | - | - | 100 |
| B | 100 | 5 | - | - | 100 |

3.2 CBCT (RATIO:-  200 / 1  A )

| Phase | Injected current in Primary (A) | Measured current in Secondary (mA) |
| --- | --- | --- |
| CBCT | 10 | 50 |

3.3 EARTH FAULT PROTECTION (E/F):- THROUGH CBCT

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| Io | 2.7 | OPERATED |

RELAY TESTING

Name Plate Details :-

| Make | ENGLISH ELECTRIC |
| --- | --- |
| Model(O/C ,E/F) | CTMM49DF5A/CTU15AF8003AD(M) |
| Sl. No. (O/C ,E/F) | M664753/M605319 |

4.0 PROTECTION TESTING:

4.1 OVER CURRENT:

Setting=   800 %                                              TMS = INST

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| R | 68 | OPERATED |
| Y | - | - |
| B | 69 | OPERATED |

4.2EARTH FAULT PROTECTION (E/F):

Setting=    1%                                              TMS=  0.1   sec

| Phase | Operation(A) | Operated Time (Sec) |
| --- | --- | --- |
| Io | 2.7 | OPERATED |

5.0 FINAL CHECKS:-

| S N | OBSERVATION | STATUS | RESULT |
| --- | --- | --- | --- |
| 1 | Complete Tightness Of Relay Panel | DONE | OK |
| 2 | Relay Measurement Testing | DONE | OK |
| 3 | Relay Protection Testing | DONE | OK |
| 4 | Relay Indications (ON/OFF/Trip) | DONE | OK |
| 5 | Relay Communication (RXD & TXD) | - | - |
| 6 | Binary Input & Binary Output Checking | - | - |
| 7 | Cleaning of Auxiliary Relay | - | - |
| 8 | Cleaning of PCB cards of Numerical Relay (if required)/Electromechanical relay | DONE | OK |
| 9 | Consolidate data & Control Scheme Checked | DONE | OK |
| 10 | Trip of CB through Master Checked | DONE | OK |
| 11 | Field Simulation of OTI/WTI/BUCH Fault Checked./ Motor Checked | - | - |
| 12 | All CT Links Closed & Tightness Check after Testing | - | - |
| 13 | All Protection Settings Normalized after Testing | DONE | OK |
| 14 | Testing DR Downloaded from the RELAY | - | - |
| 15 | Auxiliary Relay (HR & SR) operation check. | - | - |

6.0 REMARKS: -1) All test results are found satisfactory.

2) Spring charging motor found faulty informed to PSD.

.