TRANSFORMER FEEDER

- GENERAL

| LOCATION- SUBSTATION: 26 |  | CUBICAL NO.: 604 | LCP NO.: 19990 |
| --- | --- | --- | --- |
| CB NO: NA | FEEDER :- INPUT TRANSFORMER BOOSTER FAN – 1D |  |  |

TRANSFORMER TESTING

2.0 NAME PLATE DETAILS :-

| MAKE | VOLTAMP |
| --- | --- |
| TYPE | DRY |
| VECTOR GROUP | Dy11d0 |
| SL. NO. | 9911/2 |
| RATING | 1000 / 550-550 KVA |
| % IMPEDENCE | 5.39 % |
| VOLTAGE RATIO | 6600 / 710 / 710 V |
| CURRENT RATIO | 87.48 / 447.24 / 447.24 A |

2.1 WINDING RESISTANCE TEST:-

| Tap No | Measured value HV side in mΩ |  |  |  |
| --- | --- | --- | --- | --- |
|  | 1U-1V | 1V-1W | 1W-1U |
| NT | 284.3 | 283.7 | 284.2 |

| Measured value LV side Resistance in mΩ |  |  |  |
| --- | --- | --- | --- |
| LV1 | 2u-2v | 2v-2w | 2w-2u |
|  | 5.087 | 5.071 | 5.091 |
|  | 2u-2n | 2v-2n | 2w-2n |
|  | 2.563 | 2.582 | 2.514 |
| LV2 | 3u-3v | 3v-3w | 3w-3u |
|  | 5.291 | 5.240 | 5.250 |

3.0 REMARKS:-  1)  All test results are found satisfactory.

- GENERAL

| LOCATION- SUBSTATION: 26 |  | CUBICAL NO.: 604 | LCP NO.: 19990 |
| --- | --- | --- | --- |
| CB NO: NA | FEEDER :- OUTPUT TRANSFORMER TO VVVF MODE |  |  |

TRANSFORMER TESTING

2.0 NAME PLATE DETAILS :-

| MAKE | VOLTAMP |
| --- | --- |
| TYPE | DRY |
| VECTOR GROUP | Ynd11 |
| SL. NO. | 9910/2 |
| RATING | 1000 KVA |
| % IMPEDENCE | 5.17 % |
| VOLTAGE RATIO | 6.735 / 620 V |
| CURRENT RATIO | 85.72 / 931.21 A |

2.1 WINDING RESISTANCE TEST:-

| Tap No | Measured value HV side in mΩ |  |  |  |
| --- | --- | --- | --- | --- |
|  | 1U-1V | 1V-1W | 1W-1U |
| NT | 303.0 | 303.1 | 303.2 |
|  | 1U-1N | 1V-1N | 1W-1N |
|  | 152.72 | 152.63 | 152.71 |

| Measured value LV side Resistance in mΩ |  |  |
| --- | --- | --- |
| 2u-2v | 2v-2w | 2w-2u |
| 1855.7 | 1855.8 | 1856.0 |
| 2u-2n | 2v-2n | 2w-2n |
| - | - | - |

3.0 REMARKS:-  1)  All test results are found satisfactory.