- GENERAL

| LOCATION- SUBSTATION: 28 |  | CUBICAL NO. : 607 | LCP NO.: 20907 |
| --- | --- | --- | --- |
| CB NO: NA | FEEDER: ECP-1D (325 KW) |  |  |

CIRCUIT BREAKER

2.1 NAME PLATE DETAILS :-

| Make | SIEMENS |
| --- | --- |
| Type | 3AC-10N/630-500/11EU |
| Sl. No. | 00962 |
| Rated Voltage | 12KV |
| Rated Current | 630A |
| Control Voltage | 110 VDC |

2.2INSULATION RESISTANCE TEST: (MEASURED VALUES IN GΩ)

| Reference | Breaker Condition | Applied Voltage (V) | R phase | Y phase | B phase |
| --- | --- | --- | --- | --- | --- |
| Pole – Pole’ | Open | 5000 | >500 | >500 | >500 |
| Phase – Phase | Close | 5000 | >500 | >500 | >500 |
| Pole – Earth | Close | 5000 | >500 | >500 | >500 |

2.3 COIL RESISTANCE TEST:

| Terminal Reference | Measured Resistance in Ω |
| --- | --- |
| Closing coil | 270 |
| Tripping Coil | 268.8 |
| Spring charge motor | 2.9 |

2.4 CONTACT RESISTANCE TEST: 			            Applied Current (100A)

| Phase Ref. | Measured Resistance in Micro ohms |
| --- | --- |
| R | 156.6 |
| Y | 108.5 |
| B | 95.9 |

2.5 TIME INTERVAL TEST:

| Operation Ref. | Measured Time in milli Seconds |  |  |
| --- | --- | --- | --- |
|  | R | Y | B |
| Close | 95 | 94 | 95 |
| Open | 52 | 52 | 52 |
| Close – Open | 57 | 57 | 57 |

CURRENT TRANSFORMER

3. RATIO TEST: (BY PRIMARY INJECTION)

3.1 CT (CTR:    40 / 5   A)

| Phase Ref. | Injected current in Primary (A) | Measured current in Secondary ( A ) @DISPLAY |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | RELAY | ENERGY METER | ICT | AMMETER |
| R | 40 | 40 | - | - | - |
| G | 40 | 40 | - | - | 40 |
| Y | - | 40 | - | - | - |

3.2 CBCT (RATIO:  100  / 1  A)

| Injected current in Primary (A) | Measured current in Secondary (mA) |
| --- | --- |
| 10 | 0.100 |

RELAY TESTING

| MAKE | SIEMENS |
| --- | --- |
| MODEL | 7SR5711 |
| SL. NO. | GF2401516565 |

4.0 PROTECTION TESTING ( BY SECONDARY INJECTION)

4.1  MEASUREMENTS:-

| REF | INJECTED (A) | MEASURED(A) IN RELAY |
| --- | --- | --- |
| R | 5 | 40 |
| Y | 5 | 40 |
| B | 5 | 40 |

4.2 SHORT CIRCUIT:	PHIPTOC1 (50)

Set Current =    7.50      x In		Delay =    0.08 Sec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| RYB | 37.5 | 0.121 |

4.3 THERMAL O/L:	MPTTR1 (49M)

Set Current =      0.75         x In		Time const. normal =   6 min

| Phase | Injected Current (A) | Calculated Time (Sec) | Operated Time (Sec) |
| --- | --- | --- | --- |
| RYB | 23 | 10.00 | 10.028 |

4.4 NEGATIVE SEQUENCE:	MNSPTOC2  (46U/B)

Set Current =      0.3   x In       			    TMS = 0.4 Sec

| Phase | Injected Current (A) |  |  | Operated Time (Sec) |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | X2 | X4 | X6 | X2 | X4 | X6 |
| RYB | 3 | 6 | 9 | 4.38 | 1.9 | 1.03 |

4.5 STALL DURING STARTING: (14-1)

Set Current =  4.5 x In, 				 Time = 4 Sec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| RYB | 22.5 | 4.035 |

4.6 STALL DURING RUNNING: (14-2)

Set Current =  1.5 x In, 				 Time = 4 Sec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| RYB | 8 | 4.028 |

4.7 JAMMING PROTECTION:	JAMPTOC1(48)

Set Current = 2 x In		Time = 10  Sec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| RYB | 10 | 10.026 |

4.8 EARTH FAULT PROTECTION (E/F): OPERATED THROUGH CBCT

DEFLPDEF1                  Set Current =       0.020  x In A	       Time =      500 mSec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| Io | 1.9 | OPERATED |

VACUUM   CONTACTOR (NA)

5.0 NAME PLATE DETAILS :-

| Make |  |
| --- | --- |
| Type |  |
| Sl. No. |  |
| Rated Voltage |  |
| Rated Current |  |
| Control Voltage |  |

5.1 CONTACT RESISTANCE TEST: 			            Applied Current (100A)

| Phase Ref. | Measured Resistance in Micro ohms |
| --- | --- |
| R |  |
| Y |  |
| B |  |

6.0 FINAL CHECKS

| S N | OBSERVATION | STATUS | RESULT |
| --- | --- | --- | --- |
| 1 | Complete Tightness Of Relay Panel | DONE | OK |
| 2 | Relay Measurement Testing | DONE | OK |
| 3 | Relay Protection Testing | DONE | OK |
| 4 | Relay Indications (ON/OFF/Trip) | DONE | OK |
| 5 | Relay Communication (RXD & TXD) | - | - |
| 6 | Binary Input & Binary Output Checking | DONE | OK |
| 7 | Cleaning of Auxiliary Relay | - | - |
| 8 | Cleaning of PCB cards of Numerical Relay (if required) | - | - |
| 9 | Consolidate data & Control Scheme Checked | DONE | OK |
| 10 | Trip of CB through Master Checked | DONE | OK |
| 11 | Field Simulation of OTI/WTI/BUCH Fault Checked./ Motor Checked | - | - |
| 12 | All CT Links Closed & Tightness Check after Testing | DONE | OK |
| 13 | All Protection Settings Normalized after Testing | DONE | OK |
| 14 | Testing DR Downloaded from the RELAY | - | - |
| 15 | Auxiliary Relay (HR & SR) operation check. | - | - |

7.0 REMARKS:   1) All test results are found satisfactory.