- GENERAL

| LOCATION- SUBSTATION: 31 |  | CUBICAL NO. : 15 | LCP NO.: 10213 |
| --- | --- | --- | --- |
| CB NO: 60 | FEEDER NAME: TSS 2 – 5T |  |  |

CIRCUIT BREAKER

2.1NAME PLATE DETAILS:-

| Make | NGEF |
| --- | --- |
| Type | E7512/10 |
| Sl. No. | 4811240323 |
| Rated Voltage | 11 KV |
| Rated Current | 1250 A |
| Control Voltage | 220 VDC |

2.2INSULATION RESISTANCE TEST: (MEASURED VALUES IN GΩ)

| Reference | Breaker Condition | Applied Voltage (V) | R phase | Y phase | B phase |
| --- | --- | --- | --- | --- | --- |
| Pole – Pole’ | Open | 5000 | >500 | >500 | >500 |
| Phase – Phase | Close | 5000 | >500 | >500 | >500 |
| Pole – Earth | Close | 5000 | >500 | >500 | >500 |

2.3COIL RESISTANCE TEST:

| Terminal Reference | Measured Resistance in Ω |
| --- | --- |
| Closing coil | 96.0 |
| Tripping Coil | 234.0 |
| Spring charge motor | 26.6 |

2.4CONTACT RESISTANCE TEST: 			            Applied Current (100A)

| Phase Ref. | Measured Resistance in Micro ohms |
| --- | --- |
| R | 88.3 |
| Y | 50.3 |
| B | 92.6 |

2.5TIME INTERVAL TEST:

| Operation Ref. | Measured Time in milli Seconds |  |  |
| --- | --- | --- | --- |
|  | R | Y | B |
| Close | 90 | 90 | 90 |
| Open | 55 | 54 | 55 |
| Close – Open | 55 | 55 | 55 |

CURRENT TRANSFORMER

3. RATIO TEST: (BY PRIMARY INJECTION)

3.1 CT (CTR:   600  /  5   A)

| Phase Ref. | Injected current in Primary (A) | Measured current in Secondary ( A ) @ DISPLAY |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | RELAY | ENERGY METER | TRANSDUCER | AMMETER |
| R | 600 | 600 | 600 | - | - |
| Y | - | 600 | 600 | - | - |
| B | 600 | 600 | 600 | - | - |

3.2 CBCT (RATIO:     150     /   1     A)

| REFERENCE | Injected current in Primary (A) | Measured current in Secondary (mA) |
| --- | --- | --- |
| CBCT | 10 | 60 |

RELAY

| MAKE | MICOM |
| --- | --- |
| MODEL | P142 |
| SL. NO. | 140464640849028 |

4.0 PROTECTION TESTING: (SECONDARY INJECTION)

4.1 MEASUREMENTS

| REF | INJECTED (A) | MEASURED(A) IN RELAY |
| --- | --- | --- |
| R | 5 | 600 |
| Y | 5 | 600 |
| B | 5 | 600 |

4.2 INST OVERCURRENT: I > 3

Set Current = 	30.75			Delay Time = 0     mSec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| RYB | 30.75 | 0.541 |

4.3 OVERCURRENT LOW SET: I >1

Set Current=   3.75	 	     CURVE= NI	TMS =   225 mSec

| Phase | Injected Current (A) |  |  | Operated Time (Sec) |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | X2 | X4 | X6 | X2 | X4 | X6 |
| RYB | 7.5 | 15 | 22.5 | 2.293 | 1.142 | 0.887 |

4.4 EARTH FAULT PROTECTION (E/F): 	OPERATION CHECKED THROUGH CBCT

Set Current = 60 mA		Time =   0.500 Sec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| Io (CT1) | 12.5 | OPERATED |
| Io (CT1 + CT2) | 6.5 | OPERATED |

5.0 FINAL CHECKS

| S N | OBSERVATION | STATUS | RESULT |
| --- | --- | --- | --- |
| 1 | Complete Tightness Of Relay Panel | DONE | OK |
| 2 | Relay Measurement Testing | DONE | OK |
| 3 | Relay Protection Testing | DONE | OK |
| 4 | Relay Indications (ON/OFF/Trip) | DONE | OK |
| 5 | Relay Communication (RXD & TXD) | - | - |
| 6 | Binary Input & Binary Output Checking | - | - |
| 7 | Cleaning of Auxiliary Relay | DONE | OK |
| 8 | Cleaning of PCB cards of Numerical Relay (if required) | - | - |
| 9 | Consolidate data & Control Scheme Checked | DONE | OK |
| 10 | Trip of CB through Master Checked | DONE | OK |
| 11 | Field Simulation of OTI/WTI/BUCH Fault Checked./ Motor Checked | DONE | OK |
| 12 | All CT Links Closed & Tightness Check after Testing | DONE | OK |
| 13 | All Protection Settings Normalized after Testing | DONE | OK |
| 14 | Testing DR Downloaded from the RELAY | - | - |
| 15 | Auxiliary Relay (HR & SR) operation check. | - | - |

5.0 REMARKS: 1) All test results are found satisfactory.