- GENERAL

| LOCATION- SUBSTATION: 36 |  | CUBICAL NO. : 602 | LCP NO.: 12178 |
| --- | --- | --- | --- |
| CB NO: 02 | FEEDER: WATER PUMP NO. -1 D |  |  |

CIRCUIT BREAKER

2.1 NAME PLATE DETAILS :-

| Make | SIEMENS |
| --- | --- |
| Type | 3AH 3163-3 |
| Sl. No. | 17808 |
| Rated Voltage | 12 KV |
| Rated Current | 1600 A |
| Control Voltage | 110 VDC |

2.2INSULATION RESISTANCE TEST: (MEASURED VALUES IN GΩ)

| Reference | Breaker Condition | Applied Voltage (V) | R phase | Y phase | B phase |
| --- | --- | --- | --- | --- | --- |
| Pole – Pole’ | Open | 5000 | >500 | >500 | >500 |
| Phase – Phase | Close | 5000 | >500 | >500 | >500 |
| Pole – Earth | Close | 5000 | >500 | >500 | >500 |

2.3 COIL RESISTANCE TEST:

| Terminal Reference | Measured Resistance in Ω |
| --- | --- |
| Closing coil | 89.1 |
| Tripping Coil | 62.6 |
| Spring charge motor | 5.71 MΩ |

2.4 CONTACT RESISTANCE TEST: 			            Applied Current (100A)

| Phase Ref. | Measured Resistance in Micro ohms |
| --- | --- |
| R | 21.1 |
| Y | 21.9 |
| B | 21.5 |

2.5 TIME INTERVAL TEST:

| Operation Ref. | Measured Time in milli Seconds |  |  |
| --- | --- | --- | --- |
|  | R | Y | B |
| Close | 55 | 55 | 54 |
| Open | 48 | 48 | 48 |
| Close – Open | 52 | 52 | 52 |

CURRENT TRANSFORMER

3. RATIO TEST: (BY PRIMARY INJECTION)

3.1 CT (CTR:  40 / 1   A)

| Phase Ref. | Injected current in Primary (A) | Measured current in Secondary ( A ) & @DISPLAY |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | RELAY | ENERGY METER | ICT | AMMETER |
| R | 40 | 40 | - | - | 40 |
| Y | - | 40 | - | - | - |
| B | 40 | 40 | - | - | 40 |

3.2 CBCT (RATIO: 30 / 1   A)

| Injected current in Primary (A) | Measured current in Secondary (mA) |
| --- | --- |
| 10 | 333 |

RELAY TESTING

| MAKE | SIEMENS |
| --- | --- |
| MODEL | 7SK8042 53B90 – 1HEO/BB |
| SL. NO. |  |

4.0 PROTECTION TESTING ( BY SECONDARY INJECTION)

4.1  MEASUREMENTS:-

| REF | INJECTED (A) | MEASURED(A) IN RELAY |
| --- | --- | --- |
| R | 1 | 40 |
| Y | 1 | 40 |
| B | 1 | 40 |

4.2 SHORT CIRCUIT: (50-1)

Set Current =  7.00 x In		Delay =     0.04    Sec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| RYB | 7.00 | 0.053 |

4.3 THERMAL O/L: (49)

K factor  = 0.90 Time const.=  15 Min @ 2 MIN for checking

| Phase | Injected Current (A) | Calculated Time (Sec) | Operated Time (Sec) |
| --- | --- | --- | --- |
| RYB | 1.8 | 34.52 | 34.09 |

4.4 NEGATIVE SEQUENCE: ( 46-1 )

STAGE 1:	Set Current =       0.20   x In      CURVE:  DT 	    Delay = 3 Sec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| RYB | 0.20 | 3.041 |

( 46 TOC )

STAGE 2: 	Set Current =    0.50 x In       CURVE: NI         TMS = 1 Sec

| Phase | Injected Current (A) |  |  | Operated Time (Sec) |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | X2 | X4 | X6 | X2 | X4 | X6 |
| RYB | 1 | 2 | 3 | 10.123 | 4.978 | 3.731 |

4.5 PROLONGED START/ STARTUP SUPERVISION:	 (48)

Mode=	I²T	 Motor St. Current=  3.0 x In A   		   Time =   8.0 Sec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| RYB | 3.0 | 7.846 |

4.6 JAMMING PROTECTION:	JAMPTOC1

Set Current =     1.50 x In, 	Time Start Block = 8.00 Sec, 	   Time Delay = 3  Sec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| RYB | 1.50 | 11.025 |

4.7 EARTH FAULT PROTECTION (E/F): OPERATED THROUGH CBCT

(50Ns – 2)                  Set Current =     0.100  x In A	       	Time = 0.05	Sec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| Io CT1 | 3.1 | OPERATED |
| CTI + CT2 | 1.4 | OPERATED |

5.0 FINAL CHECKS

| S N | OBSERVATION | STATUS | RESULT |
| --- | --- | --- | --- |
| 1 | Complete Tightness Of Relay Panel | DONE | OK |
| 2 | Relay Measurement Testing | DONE | OK |
| 3 | Relay Protection Testing | DONE | OK |
| 4 | Relay Indications (ON/OFF/Trip) | DONE | OK |
| 5 | Relay Communication (RXD & TXD) | DONE | OK |
| 6 | Binary Input & Binary Output Checking | DONE | OK |
| 7 | Cleaning of Auxiliary Relay | - | - |
| 8 | Cleaning of PCB cards of Numerical Relay (if required) | - | - |
| 9 | Consolidate data & Control Scheme Checked | DONE | OK |
| 10 | Trip of CB through Master Checked | DONE | OK |
| 11 | Field Simulation of OTI/WTI/BUCH Fault Checked./ Motor Checked | - | - |
| 12 | All CT Links Closed & Tightness Check after Testing | DONE | OK |
| 13 | All Protection Settings Normalized after Testing | DONE | OK |
| 14 | Testing DR Downloaded from the RELAY | - | - |
| 15 | Auxiliary Relay (HR & SR) operation check. | DONE | OK |

6.0 REMARKS:   1) All test results are found satisfactory.