- GENERAL

| LOCATION- SUBSTATION: 46 |  | CUBICAL NO. : 622 | LCP NO.: 4809 |
| --- | --- | --- | --- |
| CB NO: 609 | FEEDER NAME: 46H – 1T 1000 KVA |  |  |

CIRCUIT BREAKER

2.1NAME PLATE DETAILS:-

| Make | ABB |
| --- | --- |
| Type | VD4 12.12.40 |
| Sl. No. | 1VYN020113001428 |
| Rated Voltage | 7.2 KV |
| Rated Current | 1250 A |
| Control Voltage | 220 VDC |

2.2INSULATION RESISTANCE TEST: (MEASURED VALUES IN GΩ)

| Reference | Breaker Condition | Applied Voltage (V) | R phase | Y phase | B phase |
| --- | --- | --- | --- | --- | --- |
| Pole – Pole’ | Open | 5000 | >500 | >500 | >500 |
| Phase – Phase | Close | 5000 | >500 | >500 | >500 |
| Pole – Earth | Close | 5000 | >500 | >500 | >500 |

2.3COIL RESISTANCE TEST:

| Terminal Reference | Measured Resistance in Ω |
| --- | --- |
| Closing coil | 17.4 MΩ |
| Tripping Coil | 12.0 MΩ |
| Spring charge motor | 125.0 Ω |

2.4CONTACT RESISTANCE TEST: 			            Applied Current (100A)

| Phase Ref. | Measured Resistance in Micro ohms |
| --- | --- |
| R | 17.4 |
| Y | 33.2 |
| B | 44.2 |

2.5TIME INTERVAL TEST:

| Operation Ref. | Measured Time in milli Seconds |  |  |
| --- | --- | --- | --- |
|  | R | Y | B |
| Close | 57 | 57 | 57 |
| Open | 45 | 45 | 45 |
| Close – Open | 47 | 47 | 47 |

CURRENT TRANSFORMER

3. RATIO TEST: (BY PRIMARY INJECTION)

3.1 CT (CTR:  250 / 1 A)

| Phase Ref. | Injected current in Primary (A) | Measured current in Secondary ( A ) @ DISPLAY |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | RELAY | ENERGY METER | TRANSDUCER | AMMETER |
| R | 250 | 250 | 250 | - | - |
| Y | 250 | 250 | 250 | - | 250 |
| B | 250 | 250 | 250 | - | - |

3.2 CBCT (RATIO:  100 / 1 A)

| REFERENCE | Injected current in Primary (A) | Measured current in Secondary (mA) |
| --- | --- | --- |
| CBCT | 10.0 | 98.9 |

RELAY

| MAKE | ABB |
| --- | --- |
| MODEL | REF 615 |
| SL. NO. | 1VYV91095436 |

4.0 PROTECTION TESTING: (SECONDARY INJECTION)

4.1 MEASUREMENTS

| REF | INJECTED (A) | MEASURED(A) IN RELAY |
| --- | --- | --- |
| R | 1.0 | 250.1 |
| Y | 1.0 | 249.7 |
| B | 1.0 | 249.6 |

4.2 SHORT CIRCUIT:		PHIPTOC1

Set Current =   8.40  xIn		Delay Time =   40 mSec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| RYB | 8.40 | 0.049 |

4.3 OVERCURRENT LOW SET:	DPHLPDOC1

Set Current=   0.35 x In 	 CURVE= NI		TMS = 0.30

| Phase | Injected Current (A) |  |  | Operated Time (Sec) |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | X2 | X4 | X6 | X2 | X4 | X6 |
| RYB | 0.7 | 1.4 | 2.1 | 3.027 | 1.497 | 1.159 |

4.4 EARTH FAULT PROTECTION (E/F): OPERATED THROUGH CBCT.

Set Current =  0.040  x In A		Time =  500  mSec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| Io | 4.2 | OPERATED |

LT EARTH FAULT RELAY  (NA)

| MAKE | - |
| --- | --- |
| MODEL | - |
| SL. NO. | - |

5.0 EARTH FAULT PROTECTION (E/F):

Setting=      A                                       TMS=

| Phase | Rotation(A) | Operation(A) | Injected Current (A) |  |  | Operated Time (Sec) |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | X1.5 | X2 | X4 | X1.5 | X2 | X4 |
| RYB | - | - | - | - | - | - | - | - |

TRANSFORMER TESTING

| MAKE | CROMPTON GREAVES |
| --- | --- |
| VECTOR GROUP | Yyn12 |
| SL. NO. | V8431/2 |
| RATING | 1000 KVA |
| % IMPEDENCE | 5.24 % |
| VOLTAGE RATIO | 6600 / 433 V |
| CURRENT RATIO | 87.5 / 1333.4 A |

6.1WINDING RESISTANCE TEST:

| Tap No | Measured value HV side in mΩ |  |  |
| --- | --- | --- | --- |
|  | 1U-1V | 1V-1W | 1W-1U |
| NT | 369.2 | 369.1 | 369.8 |

| Measured value LV side Resistance in uΩ |  |  |
| --- | --- | --- |
| 2u-2v | 2v-2w | 2w-2u |
| 851.8 | 853.4 | 856.6 |
| 2u-2n | 2v-2n | 2w-2n |
| 474.0 | 470.1 | 470.0 |

6.2 VOLTAGE RATIO TEST:

| TAP NO. | HV side measured voltage in volts |  |  | LV side measured voltage in volts |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1U1V | 1V1W | 1W1U | 2u – 2v | 2v – 2w | 2w – 2u | 2u – 2n | 2v – 2n | 2w – 2n |
| NT | 410.2 | 410.4 | 409.2 | 27.02 | 27.01 | 27.09 | 15.58 | 15.58 | 15.57 |

6.3 MAGNETIC BALANCE TEST: (At Normal Tap)

| HV side measured voltage in volts |  |  |
| --- | --- | --- |
| 1U-1V | 1V-1W | 1W-1U |
| 410.7 | 237.0 | 175.2 |
| 279.3 | 410.2 | 131.4 |
| 250.2 | 161.5 | 409.4 |

6.4 MAGNETIZING CURRENT TEST:-

| Applied Voltage in HV in volts |  |  |  | Measured Current in HV in Mille Amps |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Tap No | 1U-1V | 1V-1W | 1U-1W | 1U | 1V | 1W |
| NT | 410.2 | 410.4 | 409.2 | 28.5 | 20.5 | 29.6 |

LT BREAKER TESTING (NA)

7.1 NAME PLATE DETAILS:-

| Make | - |
| --- | --- |
| Type | - |
| Sl. No. | - |
| Rated Voltage | - |
| Rated Current | - |
| Control Voltage | - |

7.2 CONTACT RESISTANCE TEST: 			            Applied Current (100A)

| Phase Ref. | Measured Resistance in Micro ohms |
| --- | --- |
| R | - |
| Y | - |
| B | - |

8.0 FINAL CHECKS

| S N | OBSERVATION | STATUS | RESULT |
| --- | --- | --- | --- |
| 1 | Complete Tightness Of Relay Panel | DONE | OK |
| 2 | Relay Measurement Testing | DONE | OK |
| 3 | Relay Protection Testing | DONE | OK |
| 4 | Relay Indications (ON/OFF/Trip) | DONE | OK |
| 5 | Relay Communication (RXD & TXD) | - | - |
| 6 | Binary Input & Binary Output Checking | - | - |
| 7 | Cleaning of Auxiliary Relay | - | - |
| 8 | Cleaning of PCB cards of Numerical Relay (if required) | DONE | OK |
| 9 | Consolidate data & Control Scheme Checked | DONE | OK |
| 10 | Trip of CB through Master Checked | DONE | OK |
| 11 | Field Simulation of OTI/WTI/BUCH Fault Checked./ Motor Checked | DONE | OK |
| 12 | All CT Links Closed & Tightness Check after Testing | DONE | OK |
| 13 | All Protection Settings Normalized after Testing | DONE | OK |
| 14 | Testing DR Downloaded from the RELAY | - | - |
| 15 | Auxiliary Relay (HR & SR) operation check. | DONE | OK |

10.0 REMARKS: 1) All test results are found satisfactory.

2) REF615 relay earth fault programming done & EOR 3D Wiring shifted to REF615.

3) Reserve Panel WTI alarm and trip relay check while shorting TB found ok.