- GENERAL

| LOCATION- SUBSTATION: 73 |  | CUBICAL NO. : 613 | LCP NO.: 4667 |
| --- | --- | --- | --- |
| CB NO: 614 | FEEDER: MWP – 5D |  |  |

CIRCUIT BREAKER

2.1 NAME PLATE DETAILS :-

| Make | ABB |
| --- | --- |
| Type | VD4 12.12.40 |
| Sl. No. | 1VYN0201130000872 |
| Rated Voltage | 7.2 KV |
| Rated Current | 1250 A |
| Control Voltage | 220 VDC |

2.2INSULATION RESISTANCE TEST: (MEASURED VALUES IN GΩ)

| Reference | Breaker Condition | Applied Voltage (V) | R phase | Y phase | B phase |
| --- | --- | --- | --- | --- | --- |
| Pole – Pole’ | Open | 5000 | >500 | >500 | >500 |
| Phase – Phase | Close | 5000 | >500 | >500 | >500 |
| Pole – Earth | Close | 5000 | >500 | >500 | >500 |

2.3 COIL RESISTANCE TEST:

| Terminal Reference | Measured Resistance in mΩ |
| --- | --- |
| Closing coil | 17.2 MΩ |
| Tripping Coil | 24.6 MΩ |
| Spring charge motor | 110.2 |

2.4 CONTACT RESISTANCE TEST: 			            Applied Current (100A)

| Phase Ref. | Measured Resistance in Micro ohms |
| --- | --- |
| R | 16.8 |
| Y | 18.2 |
| B | 17.2 |

2.5 TIME INTERVAL TEST:

| Operation Ref. | Measured Time in milli Seconds |  |  |
| --- | --- | --- | --- |
|  | R | Y | B |
| Close | 53 | 53 | 53 |
| Open | 42 | 42 | 42 |
| Close – Open | 43 | 43 | 43 |

CURRENT TRANSFORMER

3. RATIO TEST: (BY PRIMARY INJECTION)

3.1 CT (CTR:    75 / 1   A)

| Phase Ref. | Injected current in Primary (A) | Measured current in Secondary ( A ) @DISPLAY |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | RELAY | ENERGY METER | ICT | AMMETER |
| R | 75 | 75 | - | - | - |
| Y | 75 | 75 | - | - | 75 |
| B | 75 | 75 | - | - | - |

3.2 CBCT (RATIO:  100  / 1  A)

| Injected current in Primary (A) | Measured current in Secondary (mA) |
| --- | --- |
| 10 | 100 |

RELAY TESTING

| MAKE | ABB |
| --- | --- |
| MODEL | REM615 |
| SL. NO. | 1VYV91095098 |

4.0 PROTECTION TESTING ( BY SECONDARY INJECTION)

4.1  MEASUREMENTS:-

| REF | INJECTED (A) | MEASURED(A) IN RELAY |
| --- | --- | --- |
| R | 1 | 75.0 |
| Y | 1 | 74.9 |
| B | 1 | 75.1 |

4.2 SHORT CIRCUIT:	PHIPTOC1

Set Current =    9.70  x In		Delay =   80  mSec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| RYB | 9.70 | 0.087 |

4.3 THERMAL O/L:	MPTTR1

Set Current =     0.97    x In		Time const. normal =   250   Sec

| Phase | Injected Current (A) | Calculated Time (Sec) | Operated Time (Sec) |
| --- | --- | --- | --- |
| RYB | 5.90 | 7.04 | 7.173 |

4.4 NEGATIVE SEQUENCE:	MNSPTOC1

STAGE 1:	     Set Current =  0.29   x In       CURVE: DT                Delay = 4000 mSec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| RYB | 0.50 | 4.013 |

MNSPTOC2

STAGE 2: 	     Set Current =   0.29  x In       CURVE: Inv. Curve B   Time =  3000 mSec

| Phase | Injected Current (A) X6 | Operated Time (Sec) |
| --- | --- | --- |
| RYB | 3 | 3.785 |

4.5 PROLONGED START/ STARTUP SUPERVISION:	  STTPMSU1

Set Current = 2.0 x In, Motor St. Current=  5.6 x In A, Start-up Time =  4 Sec, Start over delay=  10 Sec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| RYB | 5.6 | 4.004 |

4.6 JAMMING PROTECTION:	JAMPTOC1

Set Current =  2.43 x In		Time =   2000  mSec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| RYB | 2.43 | 2.009 |

4.7 EARTH FAULT PROTECTION (E/F): OPERATED THROUGH CBCT

DEFLPDEF1                  Set Current =    0.050     x In A	       Time =  500  mSec

| Phase | Injected Current (A) | Operated Time (Sec) |
| --- | --- | --- |
| Io | 5.6 | OPERATED |

5.0 FINAL CHECKS

| S N | OBSERVATION | STATUS | RESULT |
| --- | --- | --- | --- |
| 1 | Complete Tightness Of Relay Panel | DONE | OK |
| 2 | Relay Measurement Testing | DONE | OK |
| 3 | Relay Protection Testing | DONE | OK |
| 4 | Relay Indications (ON/OFF/Trip) | DONE | OK |
| 5 | Relay Communication (RXD & TXD) | - | - |
| 6 | Binary Input & Binary Output Checking | DONE | OK |
| 7 | Cleaning of Auxiliary Relay | - | - |
| 8 | Cleaning of PCB cards of Numerical Relay (if required) | - | - |
| 9 | Consolidate data & Control Scheme Checked | DONE | OK |
| 10 | Trip of CB through Master Checked | DONE | OK |
| 11 | Field Simulation of OTI/WTI/BUCH Fault Checked./ Motor Checked | - | - |
| 12 | All CT Links Closed & Tightness Check after Testing | DONE | OK |
| 13 | All Protection Settings Normalized after Testing | DONE | OK |
| 14 | Testing DR Downloaded from the RELAY | - | - |
| 15 | Auxiliary Relay (HR & SR) operation check. | DONE | OK |

6.0 REMARKS:   1) All test results are found satisfactory.

2) EOR-3D found faulty wire shifted to REM 615 relay and checked.

3) Tech trip, Emergency trip checked by shorting TB found OK. FCMA trip checked found OK but no field wire connected.